## Bowral-11 Jan 2022
BOWRAL SEWAGE TREATMENT SYSTEM
LICENCE NUMBER 1749
Licencing Period 1 May 2021 - 30 April 2022
FINAL EFFLUENT MONITORING FORTNIGHTLY TEST RESULTS (POINT 7)
SAMPLE ANALYSIS DATE |  |  |  | BOD | TSS | Ammonia | Total N | Total P | pH | Faecal coliforms | *Oil & Grease
Taken | Received | Reviewed by | Published | (mg/L) | (mg/L) | (mg/L) N | TKN+NOx (mg/L) | (mg/L) P | pH units | (CFU/100mL) | (mg/L)
2021-05-04 | 2021-05-14 | EB | 2021-05-24 | 1 | 6 | 0.37 | 5.67 | 0.095 | 7.4 | 1 | NA
2021-05-18 | 2021-05-27 | EB | 2021-06-03 | 3 | 7 | 0.62 | 6.17 | 0.18 | 7.1 | 4 | NA
2021-06-01 | 2021-06-14 | EB | 2021-06-21 | 1 | 5 | 0.48 | 7.49 | 0.109 | 7.2 | 2 | 2.5
2021-06-16 | 2021-06-28 | EB | 2021-07-04 | 4 | 8 | 0.62 | 5.92 | 0.26 | 7.2 | 1 | 2.5
2021-06-29 | 2021-07-09 | EB | 2021-07-16 | 5 | 9 | 0.42 | 6.68 | 0.193 | 7 | 1 | NA
2021-07-13 | 2021-07-22 | EB | 2021-08-02 | 3 | 8 | 0.52 | 4.12 | 0.102 | 7.3 | 1 | NA
2021-07-27 | 2021-08-04 | EB | 2021-08-13 | 4 | 8 | 0.64 | 6.4 | 0.275 | 7.4 | 4 | NA
2021-08-10 | 2021-08-19 | EB | 2021-08-27 | 6 | 7 | 0.55 | 6.48 | 0.255 | 7.4 | 5 | 2.5
2021-08-24 | 2021-09-02 | EB | 2021-09-10 | 3 | 8 | 0.95 | 5.11 | 0.202 | 7.4 | 760 | 2.5
2021-09-07 | 2021-09-17 | WM | 2021-09-29 | 3 | 6 | 0.57 | 5.24 | 0.221 | 7.3 | 3 | NA
2021-09-21 | 2021-10-02 | EB | 2021-10-12 | 3 | 7 | 1.04 | 6.64 | 0.253 | 7.4 | 1 | NA
2021-10-05 | 2021-10-12 | WM | 2021-10-21 | 1 | 2 | 0.61 | 4.29 | 0.201 | 7.4 | 1 | 2.5
2021-10-19 | 2021-10-28 | WM | 2021-11-05 | 4 | 9 | 0.59 | 4.63 | 0.238 | 7.2 | 1 | 2.5
2021-11-02 | 2021-11-23 | EB | 2021-12-01 | 2 | 8 | 0.86 | 5.71 | 0.136 | 7.3 | 380 | NA
2021-11-16 | 2021-11-26 | EB | 2021-12-09 | 3 | 7 | 0.62 | 3.27 | 0.106 | 7.4 | 1 | NA
2021-11-30 | 2021-12-09 | EB | 2021-12-17 | 3 | 7 | 0.83 | 2.92 | 0.153 | 7.4 | 2 | NA
2021-12-14 | 2021-12-29 | EB | 2022-01-07 | 5 | 6 | 0.73 | 2.99 | 0.102 | 7.3 | 5 | 2.5
2021-12-30 | 2022-01-10 | EB | 2022-01-20 | 3 | 10 | 0.53 | 3.49 | 0.122 | 7.3 | 6 | 2.5
2022-01-11 | 2022-01-20 | EB | 2022-01-27 | 1 | 4 | 1.09 | 3.67 | 0.136 | 7.3 | 2 | NA
50 percentile |  |  |  | 3 | 7 |  | 5.455 | 0.1865
80 percentile | [9 empty] | 5
90 percentile |  |  |  | 5 | 9 | 0.887 | 6.652 | 0.2565
100 percentile | [8 empty] | 7.4
Licence Target
50 percentile |  |  |  | 5 | 10 |  | 7.5 | 0.3
80 percentile | [9 empty] | 200
90 percentile |  |  |  | 10 | 15 | 2 | 10 | 0.5
100 percentile | [8 empty] | 6.5-8.5
*Oil & Grease - Only requires 6 samples per year (Feb, Apr, Jun, Aug, Oct & Dec)
Exceedance Report
Date | Parameter |  | Comment
Formulas:
SAMPLE ANALYSIS DATE = IF('[1]Bowral EPA Return'!A6,'[1]Bowral EPA Return'!A6," ")