## 31 may 2022
BUNDANOON SEWAGE TREATMENT SYSTEM
LICENCE NUMBER 2436
Licencing Period 1 May 2022 - 30 April 2023
FINAL EFFLUENT MONITORING FORTNIGHTLY TEST RESULTS (POINT 2)
SAMPLE ANALYSIS DATE |  |  |  | BOD | TSS | Ammonia | Total N | Total P | pH | Faecal coliforms | *Oil & Grease
Taken | Received | Reviewed By | Published | (mg/L) | (mg/L) | (mg/L) N | TKN+NOX | (mg/L) P | pH units | (CFU/100mL) | (mg/L)
2022-05-03 | 2022-05-12 | EB | 2022-05-20 | 1 | 3 | 0.2 | 3.61 | 0.057 | 7 | 2 | NA
2022-05-17 | 2022-05-30 | EB | 2022-06-06 | 1 | 3 | 0.2 | 3.33 | 0.058 | 7.2 | 1 | NA
2022-05-31 | 2022-06-15 | EB | 2022-06-22 | 1 | 2 | 0.16 | 4.04 | 0.081 | 7 | 1 | NA
50 percentile |  |  |  | 1 | 3 |  | 3.61 | 0.058
80 percentile | [9 empty] | 1.6
90 percentile |  |  |  | 1 | 3 | 0.2 | 3.954 | 0.0764
100 percentile | [8 empty] | 7.2
Licence Target
50 percentile |  |  |  | 7 | 10 |  | 6 | 0.2
80 percentile | [9 empty] | 200
90 percentile |  |  |  | 10 | 15 | 2 | 10 | 0.3
100 percentile | [8 empty] | 6.5-8.5
*Oil & Grease - Only requires 6 samples per year (Feb, Apr, Jun, Aug, Oct & Dec)
Exceedance Report
Date | Parameter |  | Comment