## Mittagong Website Report
MITTAGONG SEWAGE TREATMENT SYSTEM
LICENCE NUMBER 10362
Licencing Period 24 March 2023 - 23 March 2024
FINAL EFFLUENT MONITORING FORTNIGHTLY TEST RESULTS (POINT 3)
SAMPLE DATE |  |  |  | BOD | *Oil & Grease | pH | TSS | Faecal coliforms | Total N | Total P | Ammonia
Taken | Received | Reviewed by | Published | (mg/L) | (mg/L) | pH units | (mg/L) | (CFU/100mL) | TKN+NOX | (mg/L) P | (mg/L) N
2023-04-04 | 2023-04-14 | EB | 2023-04-21 | 1 | 2.5 | 6.9 | 1 | 1 | 8.79 | 0.356 | 1.29
2023-04-18 | 2023-05-02 | EB | 2023-05-15 | 1 | NA | 6.7 | 4 | 1 | 5.09 | 0.133 | 1.23
2023-05-02 | 2023-05-11 | EB | 2023-05-23 | 8 | NA | 6.6 | 6 | 1 | 3.98 | 0.153 | 0.77
2023-05-16 | 2023-05-25 | EB | 2023-06-05 | 1 | NA | 6.9 | 6 | 1 | 5.77 | 0.083 | 1.3
50 percentile |  |  |  | 1 |  |  | 5 |  | 5.43 | 0.143
80 percentile
90 percentile |  |  |  | 5.9 |  |  | 6 |  | 7.884 | 0.2951
100 percentile | [10 empty] | 1.3
Licence Target
50 percentile |  |  |  | 7 |  |  | 10 |  | 7 | 0.2
80 percentile
90 percentile |  |  |  | 10 |  |  | 15 |  | 10 | 0.3
100 percentile | [10 empty] | 6.5-8.5
*Oil & Grease - Only requires 6 samples per year (Feb, Apr, Jun, Aug, Oct & Dec)
Exceedance Report
Date | Parameter |  | Comments