## Moss Vale Website Report
MOSS VALE SEWAGE TREATMENT SYSTEM
LICENCE NUMBER 1731
Licencing Period 1 May 2023 - 30 April 2024
FINAL EFFLUENT MONITORING FORTNIGHTLY TEST RESULTS (POINT 1)
SAMPLE DATE |  |  |  | BOD | TSS | Ammonia | Total N | Total P | pH | Faecal coliforms | *Oil & Grease
Taken | Received | Reviewed by | Published | (mg/L) | (mg/L) | (mg/L) N | TKN+NOX | (mg/L) P | pH units | (CFU/100mL) | (mg/L)
2023-05-02 | 2023-05-11 | EB | 2023-05-23 | 1 | 3 | 0.63 | 6.3 | 0.52 | 7 | 4900 | NA
2023-05-16 | 2023-05-25 | EB | 2023-06-05 | 1 | 3 | 1.18 | 5.07 | 0.391 | 7.1 | 11 | NA
50 percentile |  |  |  | 1 | 3 |  | 5.685 | 0.4555
80 percentile | [9 empty] | 3922.2
90 percentile |  |  |  | 1 | 3 | 1.125 | 6.177 | 0.5071
100 percentile | [8 empty] | 7.1
Licence Target
50 percentile |  |  |  | 7 | 10 |  | 7 | 0.5
80 percentile | [9 empty] | 200
90 percentile |  |  |  | 10 | 15 | 2 | 10 | 1
100 percentile | [8 empty] | 6.5-8.5
*Oil & Grease - Only requires 6 samples per year (Feb, Apr, Jun, Aug, Oct & Dec)
Exceedance Report
Date | Parameter |  | Comment