## Berrima Pt 2 & 3 Final
BERRIMA SEWAGE TREATMENT SYSTEM - LICENCE NUMBER 3575
TEST RESULTS OF MONITORING Point 2 | [8 empty] | Point 3
Test results for final effluent May 2020 - April 2021
Parameter | BOD | TSS | Ammonia | Total N | Total P | pH | Faecal coliforms | Oil & Grease | Flow data
Units | (mg/L) | (mg/L) | (mg/L) | (mg/L) | (mg/L) | pH units | (CFU/100mL) | (mg/L) | kL/d
EPA 50%il Limit | 7 | 15 | NA | 7 | 0.5 | NA | NA | NA | NA
EPA 50%il Result | 1.5 | 6 | NA | 2.15 | 0.17 | NA | NA | NA | NA
EPA 90%il Limit | 10 | 20 | 2 | 10 | 1 | NA | NA | NA | NA
EPA 90%il Result | 4.7 | 13 | 1.06 | 5.1 | 0.35 | NA | NA | NA | NA
EPA 100%il Limit | NA | NA | NA | NA | NA | 6.5-8.5 | NA | NA | 3000
EPA 100%il Result | NA | NA | NA | NA | NA | 8.9 | NA | NA | 3 444
Minimum | 1 | 1 | 0.03 | 1.16 | 0.054 | 7.59 | 16 | 2.5 | 120
Maximum | 9 | 17 | 1.52 | 7.07 | 0.59 | 8.9 | 8900 | 2.5 | 3 444
Number of samples collected | 14 | 14 | 14 | 14 | 14 | 14 | 13 | 6 | 14
EPA monitoring frequency | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 365
Annual compliance EPA limits | Pass | Pass | Pass | Pass | Pass | Fail | Pass | Pass | Fail
Comments | Algal growth in tertiary lagoon in summer was uncontrollable with citric acid dosing. High flows were due to extreme wet weather events.
BERRIMA SEWAGE TREATMENT SYSTEM - LICENCE NUMBER 3575
TEST RESULTS OF MONITORING Point 2 | [8 empty] | Point 3
Test results for final effluent May 2019- April 2020
Parameter | BOD | TSS | Ammonia | Total N | Total P | pH | Faecal coliforms | Oil & Grease | Flow data
Units | (mg/L) | (mg/L) | (mg/L) | (mg/L) | (mg/L) | pH units | (CFU/100mL) | (mg/L) | kL/d
EPA 50%il Limit | 7 | 15 | NA | 7 | 0.5 | NA | NA | NA | NA
EPA 50%il Result | 2 | 8 | NA | 1.8 | 0.08 | NA | NA | NA | NA
EPA 90%il Limit | 10 | 20 | 2 | 10 | 1 | NA | NA | NA | NA
EPA 90%il Result | 5 | 16.4 | 0.866 | 3.2 | 0.378 | NA | NA | NA | NA
EPA 100%il Limit | NA | NA | NA | NA | NA | 6.5-8.5 | NA | NA | 3000
EPA 100%il Result | NA | NA | NA | NA | NA | 8.5 | NA | NA | 2 304
Minimum | 1 | 2.5 | 0.05 | 1 | 0.02 | 7.28 | 10 | 2.5 | 59
Maximum | 7 | 22 | 1.99 | 7.1 | 0.56 | 8.5 | 1800 | 6 | 2 304
Number of samples collected | 13 | 13 | 13 | 13 | 13 | 13 | 6 | 6 | 366
EPA monitoring frequency | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 6 | 366
Annual compliance EPA limits | Pass | Pass | Pass | Pass | Pass | Pass | Fail | Pass | Pass
Comment | Due to a error in the documentaiton 6 samples were missed in the period. Permanent controlled citric acid dosing unit to be installed.
BERRIMA SEWAGE TREATMENT SYSTEM - LICENCE NUMBER 3575
TEST RESULTS OF MONITORING Point 2 | [8 empty] | Point 3
Test results for final effluent May 2018- April 2019
Parameter | BOD | TSS | Ammonia | Total N | Total P | pH | Faecal coliforms | Oil & Grease | Flow data
Units | (mg/L) | (mg/L) | (mg/L) | (mg/L) | (mg/L) | pH units | (CFU/100mL) | (mg/L) | kL/d
EPA 50%il Limit | 7 | 15 | NA | 7 | 0.5 | NA | NA | NA | NA
EPA 50%il Result | 1 | 8 | NA | 4.09 | 0.272 | NA | NA | NA | NA
EPA 90%il Limit | 10 | 20 | 2 | 10 | 1 | NA | NA | NA | NA
EPA 90%il Result | 6.4 | 19.8 | 3.535 | 5.46 | 0.63 | NA | NA | NA | NA
EPA 100%il Limit | NA | NA | NA | NA | NA | 6.5-8.5 | NA | NA | 3000
EPA 100%il Result | NA | NA | NA | NA | NA | 9.2 | NA | NA | 1 065
Minimum | 1 | 2 | 0 | 1.7 | 0.077 | 7.7 | 2 | 2.5 | 121
Maximum | 7 | 21 | 4.3 | 5.5 | 0.63 | 9.2 | 510 | 2.5 | 1065
Number of samples collected | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 7 | 365
EPA monitoring frequency | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 6 | 365
Annual compliance EPA limits | Pass | Pass | Fail | Pass | Pass | Fail | Pass | Pass | Pass
Comment | Extreme algal growth in tertiary lagoon due to long, hot and dry summer. Citric acid dosing implemented.
BERRIMA SEWAGE TREATMENT SYSTEM - LICENCE NUMBER 3575
TEST RESULTS OF MONITORING Point 2 | [8 empty] | Point 3
Test results for final effluent May 2017- April 2018
Parameter | BOD | TSS | Ammonia | Total N | Total P | pH | Faecal coliforms | Oil & Grease | Flow data
Units | (mg/L) | (mg/L) | (mg/L) | (mg/L) | (mg/L) | pH units | (CFU/100mL) | (mg/L) | kL/d
EPA 100%il Limit | 20 | 30 | 2 | 15 | 1 | 6.5-8.5 | NA | NA | 3000
EPA 100%il Result | 5 | 20 | 0.5 | 5.11 | 0.39 | 9.5 | NA | NA | 785
Minimum | 1 | 1 | 0.12 | 1.17 | 0.054 | 7.3 | 24 | 2.5 | 17
Average | 1.6154 | 8.8462 | 0.31846 | 2.2446 | 0.14815 | 7.9846 | 75.6923 | 2.5 | 199.86
Mean | 1 | 8 | 0.32 | 2.12 | 0.112 | 7.7 | 35 | 2.5 | 191
Maximum | 5 | 20 | 0.5 | 5.11 | 0.389 | 9.5 | 360 | 2.5 | 785
Number of samples collected | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 365
EPA monitoring frequency | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 6 | 365
Annual compliance EPA limits | Pass | Pass | Pass | Pass | Pass | Fail | Pass | Pass | Pass
Comment | Extreme algal growth in tertiary lagoon due to long, hot and dry summer