## Robertson Pt 1
ROBERTSON SEWAGE TREATMENT SYSTEM - LICENCE NUMBER 20205
Point 1
Test results for September 2019-August 2020
Parameter | BOD | TSS | Ammonia | Total N | Total P | pH | Faecal coliforms | Oil & Grease | Flow data
Units | (mg/L) | (mg/L) | (mg/L) | (mg/L) | (mg/L) | pH units | (CFU/100mL) | (mg/L) | kL/d
EPA 50%il Limit | 5 | 5 | NA | 5 | 0.2 | NA | NA | NA | NA
EPA 50%il Result | 0 | 0 | NA | 3.6 | 0.08 | NA | NA | NA | NA
EPA 80%il Limit | NA | NA | NA | NA | NA | NA | 20 | NA | NA
EPA 80%il Result | NA | NA | NA | NA | NA | NA | 0 | NA | NA
EPA 90%il Limit | 10 | 10 | 1 | 10 | 0.3 | NA | NA | NA | NA
EPA 90%il Result | 0 | 0 | 0.12 | 8 | 0.12 | NA | NA | NA | NA
EPA 100%il Limit | NA | NA | NA | NA | NA | 6.5-8.5 | NA | NA | NA
EPA 100%il Result | NA | NA | NA | NA | NA | 9 | NA | NA | NA
Minimum | 0 | 0 | 0.01 | 1.4 | 0.021 | 6.9 | 0 | 0 | 324
Maximum | 0 | 0 | 0.22 | 9.12 | 0.15 | 9 | 0 | 0 | 1203
EPA monitoring frequency | Weekly sampling when discharging to the river.
Number of samples | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Annual compliance with EPA | Pass | Pass | Pass | Pass | Pass | Fail | Pass | Pass | Pass
Comments | High pH from discharge of lagoon to avoid dam failure for a breif period while not mixing with effluent due to severe storm event
ROBERTSON SEWAGE TREATMENT SYSTEM - LICENCE NUMBER 20205
Point 1
Test results for September 2018-August 2019
Parameter | BOD | TSS | Ammonia | Total N | Total P | pH | Faecal coliforms | Oil & Grease | Flow data
Units | (mg/L) | (mg/L) | (mg/L) N | TKN+NOX | (mg/L) P | pH units | (CFU/100mL) | (mg/L) | kL/d
EPA 50%il Limit | 5 | 5 | NA | 5 | 0.2 | NA | NA | NA | NA
EPA 50%il Result | No discharge | No discharge | NA | No discharge | No discharge | NA | NA | NA | NA
EPA 80%il Limit | NA | NA | NA | NA | NA | NA | 20 | NA | NA
EPA 80%il Result | NA | NA | NA | NA | NA | NA | No discharge | NA | NA
EPA 90%il Limit | 10 | 10 | 1 | 10 | 0.3 | NA | NA | NA | NA
EPA 90%il Result | No discharge | No discharge | No discharge | No discharge | No discharge | NA | NA | NA | NA
EPA 100%il Limit | NA | NA | NA | NA | NA | 6.5-8.5 | NA | NA | NA
EPA 100%il Result | NA | NA | NA | NA | NA | No discharge | NA | NA | NA
Annual compliance with EPA | There were no discharges to the environment between September 2018 - August 2019.
ROBERTSON SEWAGE TREATMENT SYSTEM - LICENCE NUMBER 20205
Point 1
Test results for September 2017-August 2018
Parameter | BOD | TSS | Ammonia | Total N | Total P | pH | Faecal coliforms | Oil & Grease | Flow data
Units | (mg/L) | (mg/L) | (mg/L) N | TKN+NOX | (mg/L) P | pH units | (CFU/100mL) | (mg/L) | kL/d
EPA 50%il Limit | 5 | 5 | NA | 5 | 0.2 | NA | NA | NA | NA
EPA 50%il Result | No discharge | No discharge | NA | No discharge | No discharge | NA | NA | NA | NA
EPA 80%il Limit | NA | NA | NA | NA | NA | NA | 20 | NA | NA
EPA 80%il Result | NA | NA | NA | NA | NA | NA | No discharge | NA | NA
EPA 90%il Limit | 10 | 10 | 1 | 10 | 0.3 | NA | NA | NA | NA
EPA 90%il Result | No discharge | No discharge | No discharge | No discharge | No discharge | NA | NA | NA | NA
EPA 100%il Limit | NA | NA | NA | NA | NA | 6.5-8.5 | NA | NA
EPA 100%il Result | NA | NA | NA | NA | NA | No discharge | NA | NA
Annual compliance with EPA | There were no discharges to the environment between September 2017- August 2018.
ROBERTSON SEWAGE TREATMENT SYSTEM - LICENCE NUMBER 20205
Point 1
Test results for September 2016-August 2017
Parameter | BOD | TSS | Ammonia | Total N | Total P | pH | Faecal coliforms | Oil & Grease | Flow data
Units | (mg/L) | (mg/L) | (mg/L) | (mg/L) | (mg/L) | pH units | (CFU/100mL) | (mg/L) | kL/d
EPA 50%il Limit | 5 | 5 | NA | 5 | 0.2 | NA | NA | NA | NA
EPA 50%il Result | 1 | 1 | NA | 2.085 | 0.155 | NA | NA | NA | NA
EPA 80%il Limit | NA | NA | NA | NA | NA | NA | 20 | NA | NA
EPA 80%il Result | NA | NA | NA | NA | NA | NA | 0.5 | NA | NA
EPA 90%il Limit | 10 | 10 | 1 | 10 | 0.3 | NA | NA | NA | NA
EPA 90%il Result | 1 | 1 | 0.065 | 4.727 | 0.29 | NA | NA | NA | NA
EPA 100%il Limit | NA | NA | NA | NA | NA | 6.5-8.5 | NA | NA | NA
EPA 100%il Result | NA | NA | NA | NA | NA | 7.4 | NA | NA | NA
Minimum | 1 | 1 | 0.05 | 1.2 | 0.05 | 6.8 | 0.5 | 0 | 245
Maximum | 1 | 2 | 0.4 | 5.04 | 0.19 | 7.4 | 86 | 0 | 280
EPA monitoring frequency | Weekly sampling when discharging to the river.
Number of samples | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 365
Annual compliance with EPA | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass