## Bowral Website Report
BOWRAL SEWAGE TREATMENT SYSTEM
LICENCE NUMBER 1749
Licencing Period 1 May 2023 - 30 April 2024
FINAL EFFLUENT MONITORING FORTNIGHTLY TEST RESULTS (POINT 7)
SAMPLE ANALYSIS DATE |  |  |  | BOD | TSS | Ammonia | Total N | Total P | pH | Faecal coliforms | *Oil & Grease
Taken | Received | Reviewed by | Published | (mg/L) | (mg/L) | (mg/L) N | TKN+NOx (mg/L) | (mg/L) P | pH units | (CFU/100mL) | (mg/L)
2023-05-02 | 2023-05-11 | EB | 2023-05-23 | 4 | 9 | 0.26 | 3.56 | 0.275 | 7.2 | 1 | NA
2023-05-16 | 2023-05-25 | EB | 2023-06-05 | 3 | 7 | 0.8 | 7.58 | 0.165 | 7.1 | 4 | NA
2023-05-30 | 2023-06-07 | EB | 2023-06-21 | 3 | 9 | 0.71 | 6.68 | 0.175 | 7.3 | 11 | NA
2023-06-13 | 2023-06-22 | WM | 2023-07-05 | 2 | 3 | 0.76 | 7.77 | 0.114 | 7.3 | 8 | NA
2023-06-27 | 2023-07-07 | WM | 2023-07-18 | 1 | 6 | 0.53 | 5.94 | 0.103 | 7.2 | 1 | 2.5
2023-07-11 | 2023-07-20 | IF | 2023-07-31 | 3 | 2 | 0.63 | 6.29 | 0.221 | 7.5 | 20 | NA
2023-07-25 | 2023-08-02 | WM | 2023-08-14 | 3 | 4 | 1.52 | 7.57 | 0.25 | 7.3 | 4 | NA
2023-08-08 | 2023-08-17 | IF | 2023-08-28 | 4 | 5 | 0.7 | 6.58 | 0.178 | 7.2 | 2 | NA
2023-08-22 | 2023-09-01 | IF | 2023-09-14 | 3 | 5 | 0.98 | 6.55 | 0.236 | 7.4 | 6 | 2.5
2023-09-06 | 2023-09-19 | WM | 2023-09-27 | 4 | 4 | 1.02 | 6.17 | 0.15 | 7.4 | 29 | NA
2023-09-19 | 2023-09-28 | WM | 2023-09-29 | 3 | 1 | 1.13 | 6.23 | 0.166 | 7.5 | 14 | NA
2023-10-03 | 2023-10-12 | LH | 2023-10-24 | 2 | 3 | 1.21 | 6.85 | 0.195 | 7.5 | 35 | NA
2023-10-17 | 2023-10-27 | LH | 2023-11-09 | 1 | 5 | 0.43 | 5.35 | 0.081 | 7.2 | 3 | 2.5
2023-10-31 | 2023-11-08 | LH | 2023-11-17 | 3 | 4 | 1.11 | 6.67 | 0.184 | 7.4 | 7 | NA
2023-11-14 | 2023-11-24 | LH | 2023-12-01 | 2 | 3 | 0.8 | 5.25 | 0.159 | 7.5 | 76 | NA
2023-11-28 | 2023-12-14 | LH | 2023-12-22 | 3 | 4 | 0.88 | 4.87 | 0.203 | 7.4 | 5 | NA
2023-12-13 | 2023-12-22 | LH | 2024-01-10 | 3 | 6 | 1.25 | 4.92 | 0.162 | 7.4 | 5 | 2.5
2023-12-27 | 2024-01-09 | WM | 2024-01-19 | 3 | 4 | 0.52 | 6.48 | 0.385 | 7.2 | 54 | NA
2024-01-09 | 2024-01-18 | LH | 2024-01-25 | 3 | 6 | 0.79 | 5.02 | 0.169 | 7.4 | 1 | NA
2024-01-23 | 2024-02-07 | LH | 2024-02-16 | 2 | 5 | 0.51 | 4.84 | 0.16 | 7.6 | 8 | NA
2024-02-06 | 2024-02-17 | LH | 2024-02-28 | 1 | 5 | 0.43 | 5.12 | 0.109 | 7.3 | 63 | 2.5
2024-02-20 | 2024-02-03 | LH | 2024-03-15 | 3 | 8 | 0.56 | 4.52 | 0.156 | 7.2 | 6 | NA
2024-03-05 | 2024-03-17 | LH | 2024-03-28 | 2 | 3 | 0.52 | 4.71 | 0.15 | 7.3 | 22 | NA
2024-03-19 | 2024-04-05 | LH | 2024-04-18 | 3 | 3 | 1.14 | 4.76 | 0.346 | 7.6 | 13 | NA
50 percentile |  |  |  | 3 | 4.5 |  | 6.055 | 0.1675
80 percentile | [9 empty] | 24.8
90 percentile |  |  |  | 3.7 | 7.7 | 1.189 | 7.354 | 0.2675
100 percentile | [8 empty] | 7.6
Licence Target
50 percentile |  |  |  | 5 | 10 |  | 7.5 | 0.3
80 percentile | [9 empty] | 200
90 percentile |  |  |  | 10 | 15 | 2 | 10 | 0.5
100 percentile | [8 empty] | 6.5-8.5
*Oil & Grease - Only requires 6 samples per year (Feb, Apr, Jun, Aug, Oct & Dec)
Exceedance Report
Date | Parameter |  | Comment