## Bundanoon Website Report
BUNDANOON SEWAGE TREATMENT SYSTEM
LICENCE NUMBER 2436
Licencing Period 1 May 2023 - 30 April 2024
FINAL EFFLUENT MONITORING FORTNIGHTLY TEST RESULTS (POINT 2)
SAMPLE ANALYSIS DATE |  |  |  | BOD | TSS | Ammonia | Total N | Total P | pH | Faecal coliforms | *Oil & Grease
Taken | Received | Reviewed By | Published | (mg/L) | (mg/L) | (mg/L) N | TKN+NOX | (mg/L) P | pH units | (CFU/100mL) | (mg/L)
2023-05-02 | 2023-05-11 | EB | 2023-05-23 | 1 | 4 | 0.8 | 3.86 | 0.178 | 7.4 | 5 | NA
2023-05-16 | 2023-05-25 | EB | 2023-06-05 | 1 | 3 | 0.25 | 5.05 | 0.226 | 7.3 | 2 | NA
2023-05-30 | 2023-06-07 | EB | 2023-06-21 | 1 | 1 | 0.38 | 4.87 | 0.149 | 7.2 | 1 | NA
2023-06-13 | 2023-06-22 | WM | 2023-07-05 | 1 | 1 | 0.69 | 5.8 | 0.114 | 7.2 | 1 | NA
2023-06-27 | 2023-07-07 | WM | 2023-07-18 | 1 | 3 | 0.16 | 4.72 | 0.093 | 7.2 | 20 | 2.5
2023-07-11 | 2023-07-20 | IF | 2023-07-31 | 1 | 2 | 0.5 | 5.89 | 0.073 | 7.1 | 1 | NA
2023-07-25 | 2023-08-02 | WM | 2023-08-14 | 1 | 1 | 0.24 | 5.42 | 0.08 | 7 | 1 | NA
2023-08-08 | 2023-08-17 | IF | 2023-08-28 | 1 | 4 | 0.2 | 5.11 | 0.077 | 7.1 | 42 | NA
2023-08-22 | 2023-09-01 | IF | 2023-09-14 | 1 | 6 | 0.25 | 5.78 | 0.158 | 7.2 | 1400 | 2.5
2023-09-06 | 2023-09-19 | WM | 2023-09-27 | 2 | 5 | 0.12 | 5.33 | 0.186 | 7.3 | 1 | NA
2023-09-19 | 2023-09-28 | WM | 2023-09-29 | 4 | 15 | 0.02 | 5.51 | 0.279 | 7.3 | 38 | NA
2023-10-03 | 2023-10-12 | LH | 2023-10-24 | 1 | 7 | 0.04 | 6.93 | 0.195 | 7.3 | 53 | NA
2023-10-17 | 2023-10-27 | LH | 2023-11-09 | 3 | 8 | 0.11 | 6.72 | 0.261 | 7.2 | 7 | 2.5
2023-10-31 | 2023-11-08 | LH | 2023-11-17 | 1 | 4 | 0.05 | 5.44 | 0.146 | 7.5 | 4 | NA
2023-11-14 | 2023-11-24 | LH | 2023-12-01 | 4 | 11 | 0.02 | 5.42 | 0.162 | 7.3 | 32 | NA
2023-11-28 | 2023-12-14 | LH | 2023-12-22 | 1 | 3 | 0.43 | 5.51 | 0.215 | 7.3 | 2 | NA
2023-12-13 | 2023-12-22 | LH | 2024-01-10 | 1 | 2 | 0.15 | 5.2 | 0.066 | 7.2 | 1 | 2.5
2023-12-27 | 2024-01-09 | WM | 2024-01-12 | 2 | 7 | 0.26 | 4.81 | 0.152 | 7.2 | 8 | NA
2024-01-09 | 2024-01-18 | LH | 2024-01-25 | 1 | 3 | 0.16 | 4.2 | 0.072 | 7.1 | 13 | NA
2024-01-23 | 2024-02-07 | LH | 2024-02-16 | 1 | 3 | 0.15 | 4.36 | 0.091 | 7.2 | 21 | NA
2024-02-06 | 2024-02-17 | LH | 2024-02-28 | 1 | 4 | 0.15 | 5.47 | 0.143 | 7.1 | 47 | 2.5
2024-02-20 | 2024-03-02 | LH | 2024-02-15 | 1 | 3 | 0.29 | 4.9 | 0.114 | 7 | 150 | NA
2024-03-05 | 2024-03-17 | LH | 2024-03-28 | 1 | 3 | 0.15 | 4.65 | 0.099 | 7.4 | 2 | NA
2024-03-19 | 2024-04-05 | LH | 2024-04-18 | 1 | 1 | 0.25 | 3.96 | 0.105 | 7.3 | 42 | NA
50 percentile |  |  |  | 1 | 3 |  | 5.265 | 0.1445
80 percentile | [9 empty] | 42
90 percentile |  |  |  | 2.7 | 7.7 | 0.479 | 5.863 | 0.2227
100 percentile | [8 empty] | 7.5
Licence Target
50 percentile |  |  |  | 7 | 10 |  | 6 | 0.2
80 percentile | [9 empty] | 200
90 percentile |  |  |  | 10 | 15 | 2 | 10 | 0.3
100 percentile | [8 empty] | 6.5-8.5
*Oil & Grease - Only requires 6 samples per year (Feb, Apr, Jun, Aug, Oct & Dec)
Exceedance Report
Date | Parameter |  | Comment
2023-08-22 | Faecal coliform |  | High faecal coliforms due to damaged UV equipment, repairs scheduled to rectifiy.