## Mittagong Website Report
MITTAGONG SEWAGE TREATMENT SYSTEM
LICENCE NUMBER 10362
Licencing Period 24 March 2023 - 23 March 2024
FINAL EFFLUENT MONITORING FORTNIGHTLY TEST RESULTS (POINT 3)
SAMPLE DATE |  |  |  | BOD | *Oil & Grease | pH | TSS | Faecal coliforms | Total N | Total P | Ammonia
Taken | Received | Reviewed by | Published | (mg/L) | (mg/L) | pH units | (mg/L) | (CFU/100mL) | TKN+NOX | (mg/L) P | (mg/L) N
2023-04-04 | 2023-04-14 | EB | 2023-04-21 | 1 | 2.5 | 6.9 | 1 | 1 | 8.79 | 0.356 | 1.29
2023-04-18 | 2023-05-02 | EB | 2023-05-15 | 1 | NA | 6.7 | 4 | 1 | 5.09 | 0.133 | 1.23
2023-05-02 | 2023-05-11 | EB | 2023-05-23 | 8 | NA | 6.6 | 6 | 1 | 3.98 | 0.153 | 0.77
2023-05-16 | 2023-05-25 | EB | 2023-06-05 | 1 | NA | 6.9 | 6 | 1 | 5.77 | 0.083 | 1.3
2023-05-30 | 2023-06-07 | EB | 2023-06-21 | 1 | NA | 7 | 7 | 1 | 5.38 | 0.096 | 1.45
2023-06-13 | 2023-06-22 | WM | 2023-07-05 | 4 | NA | 6.8 | 8 | 1 | 6.68 | 0.114 | 1.8
2023-06-27 | 2023-07-07 | WM | 2023-07-18 | 4 | 2.5 | 6.8 | 9 | 1 | 6.2 | 0.105 | 1.78
2023-07-11 | 2023-07-20 | IF | 2023-07-31 | 2 | NA | 6.6 | 9 | 1 | 7.4 | 0.077 | 1.55
2023-07-25 | 2023-08-02 | WM | 2023-08-14 | 1 | NA | 6.8 | 8 | 1 | 7.19 | 0.107 | 1.5
2023-08-08 | 2023-08-17 | IF | 2023-08-28 | 1 | NA | 6.9 | 7 | 2 | 9.69 | 0.126 | 1.98
2023-08-22 | 2023-09-01 | WM | 2023-09-14 | 4 | 2.5 | 6.8 | 8 | 1 | 6.51 | 0.136 | 1.54
2023-09-06 | 2023-09-19 | WM | 2023-09-27 | 1 | NA | 6.9 | 7 | 9 | 5.92 | 0.17 | 1.23
2023-09-19 | 2023-09-28 | WM | 2023-09-29 | 1 | NA | 7.2 | 7 | 220 | 6 | 0.253 | 1.54
2023-10-03 | 2023-10-12 | LH | 2023-10-24 | 1 | NA | 6.8 | 6 | 3 | 6.19 | 0.127 | 1.6
2023-10-17 | 2023-10-27 | LH | 2023-11-09 | 1 | 2.5 | 6.9 | 6 | 2 | 6.93 | 0.16 | 1.66
2023-10-31 | 2023-11-08 | LH | 2023-11-17 | 1 | NA | 6.4 | 7 | 1 | 6.17 | 0.07 | 1.49
2023-11-14 | 2023-11-24 | LH | 2023-12-01 | 1 | NA | 6.9 | 6 | 20 | 7.46 | 0.15 | 1.4
2023-11-28 | 2023-12-14 | LH | 2023-12-22 | 1 | NA | 7.3 | 5 | 6 | 6.17 | 0.353 | 1.2
2023-12-13 | 2023-12-22 | LH | 2024-01-10 | 1 | 2.5 | 7.1 | 4 | 4 | 6.5 | 0.118 | 1.96
2023-12-27 | 2024-01-09 | WM | 2024-01-12 | 3 | NA | 6.9 | 14 | 1 | 4.58 | 0.545 | 1.28
2024-01-09 | 2024-01-18 | LH | 2024-01-25 | 1 | NA | 6.8 | 10 | 3 | 4.65 | 0.2 | 1.45
2024-01-23 | 2024-02-07 | LH | 2024-02-16 | 3 | NA | 6.8 | 18 | 2 | 5.51 | 0.258 | 1.79
2024-02-06 | 2024-02-17 | LH | 2024-02-28 | 5 | 2.5 | 6.8 | 14 | 3 | 7.88 | 0.54 | 2.11
2024-02-20 | 2024-03-02 | LH | 2024-02-15 | 1 | NA | 6.5 | 5 | 2 | 4.32 | 0.029 | 0.54
2024-03-05 | 2024-03-17 | LH | 2024-03-28 | 1 | NA | 6.9 | 4 | 1 | 6.72 | 0.045 | 1.26
2024-03-19 | 2024-04-05 | LH | 2024-04-18 | 1 | NA | 7 | 5 | 1 | 5.88 | 0.112 | 1.08
50 percentile |  |  |  | 1 |  |  | 7 |  | 6.18 | 0.13
80 percentile | [7 empty] | 200
90 percentile |  |  |  | 4 |  |  | 12 |  | 7.67 | 0.3545
100 percentile | [10 empty] | 2.11
Licence Target
50 percentile |  |  |  | 7 |  |  | 10 |  | 7 | 0.2
80 percentile | [7 empty] | 200
90 percentile |  |  |  | 10 |  |  | 15 |  | 10 | 0.3
100 percentile | [10 empty] | 6.5-8.5
*Oil & Grease - Only requires 6 samples per year (Feb, Apr, Jun, Aug, Oct & Dec)
Exceedance Report
Date | Parameter |  | Comments