## Moss Vale Website Report
MOSS VALE SEWAGE TREATMENT SYSTEM
LICENCE NUMBER 1731
Licencing Period 1 May 2023 - 30 April 2024
FINAL EFFLUENT MONITORING FORTNIGHTLY TEST RESULTS (POINT 1)
SAMPLE DATE |  |  |  | BOD | TSS | Ammonia | Total N | Total P | pH | Faecal coliforms | *Oil & Grease
Taken | Received | Reviewed by | Published | (mg/L) | (mg/L) | (mg/L) N | TKN+NOX | (mg/L) P | pH units | (CFU/100mL) | (mg/L)
2023-05-02 | 2023-05-11 | EB | 2023-05-23 | 1 | 3 | 0.63 | 6.3 | 0.52 | 7 | 4900 | NA
2023-05-16 | 2023-05-25 | EB | 2023-06-05 | 1 | 3 | 1.18 | 5.07 | 0.391 | 7.1 | 11 | NA
2023-05-30 | 2023-06-07 | EB | 2023-06-21 | 1 | 5 | 0.64 | 6.96 | 0.65 | 7.3 | 250 | NA
2023-06-13 | 2023-06-22 | WM | 2023-07-05 | 4 | 3 | 0.33 | 4.73 | 0.434 | 7 | 1 | NA
2023-07-26 | 2023-07-07 | WM | 2023-07-18 | 1 | 6 | 0.89 | 6.04 | 0.295 | 7.1 | 16 | 2.5
2023-07-11 | 2023-07-20 | IF | 2023-07-31 | 4 | 5 | 0.7 | 4.26 | 0.276 | 7.3 | 8 | NA
2023-07-25 | 2023-08-02 | WM | 2023-08-14 | 5 | 12 | 0.11 | 3.66 | 0.344 | 7.2 | 1 | NA
2023-08-08 | 2023-08-17 | IF | 2023-08-28 | 3 | 6 | 0.95 | 10.5 | 0.71 | 7.3 | 1 | NA
2023-08-22 | 2023-09-01 | WM | 2023-09-14 | 3 | 7 | 1.35 | 6.78 | 0.378 | 7.3 | 1 | 2.5
2023-09-06 | 2023-06-19 | WM | 2023-09-27 | 1 | 3 | 1.88 | 4.28 | 0.165 | 7.5 | 1 | NA
2023-09-19 | 2023-09-28 | WM | 2023-09-29 | 1 | 5 | 1.17 | 6.54 | 0.284 | 7.3 | 1 | NA
2023-10-03 | 2023-10-12 | LH | 2023-10-24 | 1 | 1 | 1.2 | 7.15 | 0.665 | 7.6 | 1 | NA
2023-10-17 | 2023-10-27 | LH | 2023-11-09 | 1 | 4 | 1.47 | 4.95 | 0.205 | 7.2 | 27 | 2.5
2023-10-31 | 2023-11-08 | LH | 2023-11-17 | 1 | 4 | 0.71 | 5.81 | 0.482 | 7.3 | 1 | NA
2023-11-14 | 2023-11-24 | LH | 2023-12-01 | 1 | 6 | 1.13 | 4.02 | 0.23 | 7.4 | 15 | NA
2023-11-28 | 2023-12-14 | LH | 2023-12-22 | 1 | 1 | 0.97 | 1.81 | 0.158 | 7.3 | 5 | NA
2023-12-13 | 2023-12-22 | LH | 2024-01-10 | 1 | 4 | 1.99 | 3.23 | 0.178 | 7.1 | 32 | 2.5
2023-12-27 | 2024-01-09 | WM | 2024-01-12 | 1 | 3 | 1.87 | 5.75 | 0.26 | 7.1 | 280 | NA
2024-01-09 | 2024-01-18 | LH | 2024-01-25 | 1 | 1 | 1.24 | 5.17 | 0.175 | 7.4 | 70 | NA
2024-01-23 | 2024-02-07 | LH | 2024-02-16 | 1 | 3 | 0.4 | 4.91 | 0.109 | 7 | 14 | NA
2024-02-06 | 2024-02-17 | LH | 2024-02-28 | 1 | 7 | 0.92 | 5.44 | 0.234 | 7.1 | 5300 | 2.5
2024-02-20 | 2024-03-02 | LH | 2024-03-15 | 1 | 3 | 0.94 | 7.99 | 0.21 | 7 | 18 | NA
2024-03-05 | 2024-03-17 | LH | 2024-03-28 | 1 | 1 | 0.49 | 7.07 | 0.245 | 7.4 | 23 | NA
2024-03-19 | 2024-04-05 | LH | 2024-04-18 | 1 | 2 | 0.31 | 8.13 | 0.145 | 7.2 | 1 | NA
50 percentile |  |  |  | 1 | 3.5 |  | 5.595 | 0.268
80 percentile | [9 empty] | 47.2
90 percentile |  |  |  | 3.7 | 6.7 | 1.75 | 7.738 | 0.611
100 percentile | [8 empty] | 7.6
Licence Target
50 percentile |  |  |  | 7 | 10 |  | 7 | 0.5
80 percentile | [9 empty] | 200
90 percentile |  |  |  | 10 | 15 | 2 | 10 | 1
100 percentile | [8 empty] | 6.5-8.5
*Oil & Grease - Only requires 6 samples per year (Feb, Apr, Jun, Aug, Oct & Dec)
Exceedance Report
Date | Parameter |  | Comment
2023-08-08 | Total nitrogen |  | Delayed sample delivery to lab elevated TN results on this occasion.